Product: 734C1

# DS-3 and DS-4, 734C Series, #20-1 SPC Coax, CMR/CMG

# Product Description

20 AWG solid .032" silver-plated copper conductors, gas-injected FHDPE insulation, Duobond®; tinned copper braid shield (85% coverage), inner PVC jacket, overall PVC jacket with ripcord.

# Technical Specifications

Product Overview

| Suitable Applications: | Central Office wiring for DS3 transmissions. |
| --- | --- |

Physical Characteristics (Overall)

Conductor

| AWG | Stranding | Material | Nominal Diameter |  | No. of Coax |  |
| --- | --- | --- | --- | --- | --- | --- |
| 20 | Solid | SCCS - Silvered Copper Covered Steel | 0.032 in |  | 1 |  |
| Conductor Count: |  |  |  | 1 |  |  |

Insulation

| Material | Nominal Diameter |  |  |
| --- | --- | --- | --- |
| PE - Polyethylene (Foam) | 0.148 in |  |  |
| Table Notes: |  |  | Gas Injected |

Inner Shield

| Type | Layer | Material | Material Trade Name |  | Coverage [%] |  |
| --- | --- | --- | --- | --- | --- | --- |
| Tape | 1 | Tri-Laminate (Alum+Poly+Alum) | Duobond® |  | 100% |  |
| Braid | 2 | Tinned Copper (TC) |  |  | 85% |  |
| Table Notes: |  |  |  | Tape bonded to dielectric |  |  |

Inner Jacket

| Material | Nominal Diameter |
| --- | --- |
| PVC - Polyvinyl Chloride | 0.235 in |

Outer Shield

No Shield

Material

Outer Jacket

| Material | Nominal Diameter | Ripcord |
| --- | --- | --- |
| PVC - Polyvinyl Chloride | 0.235 in | Yes |

Electrical Characteristics

Conductor DCR

| Nominal Conductor DCR | Nominal Conductor DCR Conductor Resistance | Nominal Inner Shield DCR | Outer Conductor DCR |
| --- | --- | --- | --- |
| 10 Ohm/1000ft | 10 Ohm/1000ft | 2.4 Ohm/1000ft | 2.4 Ohm/1000ft |

Capacitance

16.8 pF/ft

Nom. Capacitance Conductor to Shield

Inductance

0.097 µH/ft

Nominal Inductance

Impedance

75 Ohm

Nominal Characteristic Impedance

Return Loss (RL)

| Frequency [MHz] | Minimum Return (RL) |
| --- | --- |
| 5-150 MHz | 32 dB |

Delay

| Nominal Delay | Nominal Velocity of Propagation (VP) [%] |
| --- | --- |
| 1.27 ns/ft | 80% |

High Frequency

| Frequency [MHz] | Max. Insertion Loss (Attenuation) |
| --- | --- |
| 1 MHz | 0.28 dB/100ft |
| 5 MHz | 0.59 dB/100ft |
| 10 MHz | 0.8 dB/100ft |
| 22.5 MHz | 1.18 dB/100ft |
| 50 MHz | 1.82 dB/100ft |
| 100 MHz | 2.6 dB/100ft |
| 150 MHz | 3.22 dB/100ft |

Voltage

300 V RMS

UL Voltage Rating

Temperature Range

| Operating Temperature Range: | -40°C To +75°C |
| --- | --- |

Mechanical Characteristics

| Bulk Cable Weight: | 30 lbs/1000ft |
| --- | --- |
| Max. Pull Tension: | 60 lbs |
| Min Bend Radius (Overall): | 2.5 in |

Standards

| NEC/(UL) Compliance: | CMR |
| --- | --- |
| CEC/C(UL) Compliance: | CMG |
| RG Type: | 59 |

Applicable Environmental and Other Programs

| Environmental Space: | Indoor - Riser |
| --- | --- |
| EU Directive 2000/53/EC (ELV): | Yes |
| EU Directive 2003/11/EC (BFR): | Yes |
| EU Directive 2011/65/EU (RoHS 2): | Yes |
| EU Directive 2012/19/EU (WEEE): | Yes |
| EU Directive 2015/863/EU (RoHS 2 amendment): | Yes |
| EU Directive Compliance: | EU Directive 2003/11/EC (BFR) |
| EU CE Mark: | Yes |
| MII Order #39 (China RoHS): | Yes |

Suitability

| Suitability - Indoor: | Yes |
| --- | --- |

Flammability, LS0H, Toxicity Testing

| UL Flammability: | UL1666 Vertical Shaft |
| --- | --- |
| CSA Flammability: | FT4 |
| UL voltage rating: | 300 V RMS |

Plenum/Non-Plenum

| Plenum (Y/N): | No |
| --- | --- |

Related Part Numbers

Variants

| Item # | Color | Put-Up Type | Length | UPC |
| --- | --- | --- | --- | --- |
| 734C1 0081000 | Gray | Reel | 1,000 ft | 612825184225 |
| 734C1 0083000 | Gray | Reel | 3,000 ft | 612825184232 |
| 734C1 0085000 | Gray | Reel | 5,000 ft | 612825184256 |

| Footnote: | C - CRATE REEL PUT-UP. |
| --- | --- |

History

| Update and Revision: | Revision Number: 0.334 Revision Date: 11-09-2022 |
| --- | --- |

© 2024 Belden, Inc All Rights Reserved.

Although Belden makes every reasonable effort to ensure their accuracy at the time of this publication, information and specifications described here in are subject to error or omission and to change without notice, and the listing of such information and specifications does not ensure product availability.

Belden provides the information and specifications herein on an "ASIS" basis, with no representations or warranties, whether express, statutory or implied. In no event will Belden be liable for any damages (including consequential, indirect, incidental, special, punitive, or exemplary damages) whatsoever, even if Belden has been advised of the possibility of such damages, whether in an action under contract, negligence or any other theory, arising out of or in connection with the use, or inability to use, the information or specifications described herein.

All sales of Belden products are subject to Belden's standard terms and conditions of sale.

Belden believes this product to be in compliance with all applicable environmental programs as listed in the data sheet. The information provided is correct to the best of Belden's knowledge, information and belief at the date of its publication. This information is designed only as a general guide for the safe handling, storage, and any other operation of the product itself or the one that it becomes a part of. The Product Disclosure is not to be considered a warranty or quality specification. Regulatory information is for guidance purposes only. Product users are responsible for determining the applicability of legislation and regulations based on their individual usage of the product.